## Slide 1: Section 3: Introduction to Bayesian Inference
Purpose
  Present the subjectivist interpretation of probability, Bayesian inference for single-parameter problems, use of Excel functions, and applications to commonly encountered probabilistic models
Objectives: Students will learn
  Probability interpreted as a quantification of state of knowledge
  Bayes’ Theorem, Bayesian inference for parameter values in following:
    Binomial, Poisson, and exponential (aleatory) models
    Relation of these models to likelihood function in Bayes’ Theorem
  Use of discrete priors
  Conjugate priors for Poisson, binomial, and exponential likelihoods
  Formal priors for Poisson, binomial, and exponential data
  Use of spreadsheets to update conjugate priors
  Use of online RADS calculator for updating conjugate priors and nonconjugate lognormal priors

## Slide 2: Elementary Bayesian Statistical Inference
Topics to be covered
  Subjective interpretation of probability
  Bayes’ Theorem as mechanism for Bayesian inference
  Likelihood functions (aleatory models)
    Binomial distribution
    Poisson distribution
    Exponential distribution
  Prior distributions (epistemic uncertainty)
    Discrete
    Conjugate
    Formal
    Nonconjugate
George Apostolakis

## Slide 3: Bayesian Statistical Inference
General framework is covered in HOPE…
  Page 6-2 (one-page introduction)
  Section 6.2.2 for initiating events and running failures
    Failure to run is also covered in Section 6.5
  Section 6.3.2 for failures on demand
  Section B.5 for summary of Bayesian estimation

## Slide 4: Motivation for Bayesian Inference
Problems with frequentist inference
  If data are sparse, estimates can be unrealistic (0 events in some cases)
  No way to incorporate nonempirical “data”
    For example, expert judgment
  Difficult to propagate uncertainties (i.e., confidence intervals) through logic models
Solution: A different interpretation of “probability”
  Information about the parameter, beyond what is in the empirical data, is included in the estimate
  Use Monte Carlo sampling to propagate uncertainties (expressed as probability distributions) through logic models

## Slide 5: Subjective Probability
In the Bayesian, or “subjectivist,” approach, probability is a quantification of state of knowledge
  It is used to describe the plausibility of an event
    Plausibility – “Apparent validity”
  A mechanism to encode information
Note that, for “Bayes’ Theorem,”
  Thomas Bayes
  never wrote it
  Laplace first used
  it in real problems
Adapted from “Probability and Measurement Uncertainty in Physics” by Giulio D’Agostini, December 1995

## Slide 6: Bayesian Parameter Estimation
The general procedure is:
  Begin with an aleatory model for the process of interest
  Specify a prior distribution for parameter(s) in this model, quantifying epistemic uncertainty, i.e., quantifying state of knowledge about the possible parameter values
  Collect data
  Obtain the posterior (i.e., updated) distribution for the parameter(s) of interest
  Check validity of model (P-501 and P-502 courses)
We follow this process to make inferences, that is, to determine the probability that a model or hypothesis is reasonable, conditional on all available evidence

## Slide 7: Common Aleatory Models in PRA
Binomial
Poisson
Exponential
We will use these models to “count” failures

## Slide 8: What can we count?
Examples of Poisson processes
  Counting particles such as neutrons or photons
  Number of (lit) lights failing
  Arrival of customers
  Large earthquakes
  HTTP requests on a server
  Loss of Offsite Power
Examples of Bernoulli (binomial) processes
  Tossing a coin
  Starting a car
  Discrete random walk
  Turning on a light
  Birth of a child
  Launching a rocket
  Failures of a EDG

## Slide 9: A “roadmap” (from NASA/SP-2009-569)

## Slide 10: Binomial Distribution
Commonly used model for failure to change state.
Assumptions about the physical process
  On each demand, outcome is a failure with probability p (alternatively, a success with probability q=1  p)
    This p is the same on every demand
    Called a Bernoulli trial
  Occurrences of failures on different demands are independent
Form of the data
  We observe a random number of failures, X, in a fixed or specified number of demands n
Pages 2-7 through 2-10, A-12 through A-13

## Slide 11: Binomial Distribution: Functional Form
Then the random variable X has a binomial(n, p) distribution:
for x = 0, 1, …, n
(x = number of failures)
Distribution parameters are p (unknown) and n (specified)
For Bayesian inference, we write f(x) as f(x|p), called the likelihood function, sometimes denoted L(p)
  Leads to frequentist maximum likelihood estimate (MLE) for p of x/n
X is observed (failures) and p is unknown (focus of inference)

## Slide 12: Binomial Coefficient
The binomial coefficient is defined as
Example
  Note that 0! = 1

## Slide 13: Binomial Distribution: Examples
n = 10, p = 0.3
n = 100, p = 0.3

## Slide 14: Binomial Distribution: Summary Measures
Moments
  Mean = np
  Variance = np(1-p)
Probability
  To find probability of seeing exactly x outcomes in n number of trials [or Pr(X=x | n, p)] use
    =BINOMDIST(x, n, p, FALSE) in Excel
    To find the cumulative of this use [Pr(0≤X≤x)]
      =BINOMDIST(x, n, p, TRUE) in Excel
  To find approximate (100z)th percentile of X use
    =CRITBINOM(n, p, z) in Excel
    Example, to find 95th
      =CRITBINOM(n, p, 0.95)

## Slide 15: Poisson Distribution
Most commonly used aleatory model for initiating events and failure to operate for specified time period
Assumptions on the physical process
  Probability of event in short time period t is approximately t, for a constant 
  Simultaneous events do not occur
  Occurrences of events in disjoint time periods are independent
Form of the data
  We observe a random number of events, X, in a fixed or specified time period t
X is observed and  is unknown (focus of inference)
Pages 2-2 through 2-7, A-13 through A-14

## Slide 16: Poisson Distribution: Functional Form
Then the random variable X has a Poisson(t) distribution:
for x = 0, 1, 2, …
(x = number of events)
The distribution depends on one quantity, t, ( unknown, t specified)
  Therefore, product t is sometimes written as  (or even ), and the distribution is called Poisson()
For Bayesian inference, we write f(x) as f(x|), called the likelihood function, sometimes denoted L()
  Leads to frequentist MLE for  of x/t

## Slide 17: Poisson Distribution: Examples
mu = 3
mu = 30

## Slide 18: Poisson Distribution: Summary Measures
Moments
  Mean = t = 
  Variance = t = 
Probability
  To find probability of seeing exactly x outcomes in time t [or Pr(X=x | t, )] use
    =POISSON(x, mean, FALSE) in Excel
    To find the cumulative of this use [Pr(0≤X≤x)]
      =POISSON(x, mean, TRUE) in Excel
  To find approximate (100z)th percentile of X?
    There is no “CRITPOISSON” in Excel, so need to look at the cumulative distribution to determine this

## Slide 19: DSW Poisson Example #1
To find Pr(X=2 | t=10 yr, λ=0.3/yr)

## Slide 20: DSW Poisson Example #2
To find Pr(X ≤ 2 | t=10 yr, λ=0.3/yr)

## Slide 21: Exponential Distribution
A commonly used aleatory model for a time duration
  Time to repair component, time to suppress fire, etc.
Very simple (sometimes too simple)
Setting: Watch something until an event of interest occurs, for example
  Failure to run
  Restoration of power
  Suppression of fire, etc.
Let T be a random variable representing time when event occurs
Pages 2-17, A-17 through A-18

## Slide 22: Exponential Distribution: Genesis
Assumption on the physical process
  1. For t  0 and small t
    Pr( T  t + t | T > t)   t (for a constant )
Interpretation
  If the system is running at time t, probability that system will fail in next small time interval t is t, regardless of what t is.
  That is, the system does not improve or degrade (i.e., age) as a function of time
Form of the data
  We observe the event times, Ti, i = 1, 2,…, n
T is observed,  is unknown (the focus of inference)

## Slide 23: Exponential Distribution: Graphs
Under the assumptions from the previous page
  T has an exponential() distribution
  for t ≥ 0 for t ≥ 0
Area = 1.0
Area = 1.0

## Slide 24: Exponential Distribution
Units
  “ t” is unitless
   has units of 1/t (in PRA, usually per hour)
    Initiating events are often per year
Alternative parameterization in terms of μ = 1/ .
  Just rewrite formulas in obvious way
  Units of μ are units of t
    Also known as “mean time to failure” (MTTF)
Moments
  Mean = 1/ = μ
  Variance = 1/2 = μ2

## Slide 25: Exponential Distribution: Likelihood Function
Likelihood function for n observed times, ti
Leads to frequentist MLE for  of n / ti

## Slide 26: Bayes’ Theorem and Bayesian Parameter Estimation – Discrete Case
Consider the unknown parameter  (same idea if the parameter is p)
For now, assume X (observed variable) is discrete, with f(x| ) = Pr(X=x| )
Also assume that the unknown parameter λ can only take discrete values,  1,  2, …
Define discrete prior distribution, πprior( i ) = Pr( =  i ).
By Bayes’ Theorem,
or
Denominator is a normalizing constant

## Slide 27: Bayes’ Theorem and Bayesian Parameter Estimation – General Case
Define πprior(), the prior pdf of 
  Discrete, continuous, or mixed
Let f(x | ) be the pdf of X, dependent on 
  This is the likelihood or aleatory model
The posterior pdf of  is
πpost is proportional to the product of the prior distribution and the likelihood function
  πpost is what we put into our PRA basic events
Notes: For mixed prior, integral separates into integral over continuous part (Lebesgue measure) and sum over discrete part (counting measure) (i.e., Lebesgue-Stieltjes integral).

## Slide 28: Bayes’ Theorem is Basis for Bayesian Updating of Data
Bayes’ Theorem:
Where:
  q is parameter of interest
  po(q) is prior distribution
  L(E|q) is likelihood function
  p1(q|E) is posterior distribution (updated estimate)

## Slide 29: Probability Distributions Represent Uncertainty
Usually used to represent state of knowledge of parameter values
  Model assumptions typically addressed via sensitivity studies
Probability distribution () represents analyst’s uncertainty about unknown value of 
  Note that  may not be observable (for example, if a failure rate)
Large uncertainty
Less uncertainty
No uncertainty

## Slide 30: Bayes’ Theorem and Bayesian Parameter Estimation – General Case
If prior distribution is continuous
  Parameter (e.g., ) has values over a continuous range (and a continuum of possible values).
Even though our goal is to obtain posterior distribution [πpost( | x)] for a parameter λ, need to remember
  λ is assigned a prior distribution (representing information about possible values of λ)
    Often convenient to summarize distribution by metrics such as mean, variance, or percentiles
  Note that the distribution (of PRA parameters) is usually subjective, not a real, physical or empirical distribution
    We do not “see” probabilities

## Slide 31: Historical Use of Bayes Theorem
Laplace, in 1774, used Bayesian methods to estimate the mass of Saturn
  Assumed uniform prior density (what was known at the time)
  Data consisted of mutual perturbations between Jupiter and Saturn
His result was that he gave odds of 11,000 to 1 that his mass estimate* is not in error by more than 1%
  What do odds of 11,000 to 1 imply?
    That the point estimate ± 1% is the 99.99% credible interval
200 years of science increased his estimate by about 0.6%
  Laplace would have won his bet (so far!)
*1/3512th of solar mass = 5.7  1026 kg
Pierre Laplace

## Slide 32: Odds?
Odds typically thought of as a “betting” term
  Really a way to sneak probability into a discussion!
  This is the odds for something
Notes: “Odd of dying,” National Safety Council

## Slide 33: Odds?
Odds typically thought of as a “betting” term
  Really a way to sneak probability into a discussion!
  This is the odds for something
“Odds of Dying”
National Safety Council 2017
Total odd of dying (any cause)
Notes: “Odd of dying,” National Safety Council

## Slide 34: Uses of Posterior Distribution
For presentation purposes
  Plot the posterior pdf
  Give the posterior mean
  Give a Bayes credible interval, an interval that contains most of the posterior probability (e.g. 90% or 95%)
    90% interval  <5th, 95th>
    95% interval  <2.5th, 97.5th>
For risk assessment
  Sample from the distribution of each parameter
  Combine the results to obtain sample from Bayes distribution of end-state frequency
Notes: We do not discuss highest posterior density (HPD) intervals in this class.

## Slide 35: Prior Distributions
We are going to examine three different situations related to different types of prior information
  Discrete priors
  Conjugate priors
    Informative
    Noninformative (or formal)
  Nonconjugate priors

## Slide 36: Discrete Prior Distributions
These priors are easy to update with a spreadsheet (e.g., Excel)
  Follows directly from Bayes’ Theorem
    For example, see “discrete prior.xls” in Excel folder
Numerator in Bayes’ Theorem is product of likelihood and prior probability of  i
  To obtain full posterior probability, divide every such product by the sum of all such products
  This makes the posterior probabilities (for all possible values of i ) sum to 1.0
Discrete priors were once common in risk assessment
  Not used much these days
Pages 6-9 through 6-11, 6-33 through 6-35
discrete prior.xls

## Slide 37: Example of Discrete Prior and Posterior
Page 6-10
Coarse discrete prior for λ (events per year)
Posterior for λ, based on 10 observed events in 6 years

## Slide 38: Conjugate Priors

## Slide 39: Conjugate Priors
Prior and posterior distribution have same functional form
  Only distribution parameters change to reflect data incorporated via likelihood function
    This means you can write down the posterior distribution with just arithmetic
    Mathematically convenient (no integration)
  Widely used in PRA (perhaps too widely)
In this section, we will address conjugate priors for three aleatory models commonly used in PRA
  Binomial distribution
  Poisson distribution
  Exponential distribution
Notes: Mention that conjugate priors exist for other models.

## Slide 40: Binomial Likelihood – Beta Conjugate Prior
Facts about beta(, β) distribution
  beta(, β) density
    f(p) = C pα-1(1-p)β-1
  Mean:  / ( + β)
  Variance: mean(1 – mean)/( + β + 1)
  Percentiles from tables in
  HOPE, App. C
  Easier and more accurate
  to use BETAINV in Excel:
  100p percentile = BETAINV(p, , )
  SAPHIRE uses mean and  (called “b” by SAPHIRE)
Pages A-21 through A-22, C-8 through C-13

## Slide 41: Binomial Likelihood – Beta Conjugate Prior
If X is binomial(n, p) and gprior(p) is beta(prior, βprior)
  Then posterior distribution of p is
    beta(post, βpost)
      post = prior + x (x = # events)
      βpost = βprior + n - x (n = total # trials)
    prior is like prior number of events
    prior is like prior number of successes
    Posterior mean is (prior + x)/(prior + βprior + n)
    This is a weighted average of MLE, x/n,
    and prior mean, prior /(prior + βprior )
Pages 6-35 through 6-37
Notes: Prove this heuristically by writing posterior as product of prior and likelihood. Don’t worry about normalization constant.

## Slide 42: DSW Binomial-Beta Bayesian Example
Assume our prior is ~Beta(1, 1)
Assume we see 15 failures in 87 demands
Step 1 – Specify the Prior (Beta Tab)
Step 2 – Specify Data (Bayes-Binomial)

## Slide 43: DSW Binomial-Beta Bayesian Example
Read the results

## Slide 44: Poisson Likelihood – Gamma Conjugate Prior
Facts about gamma(, β) distribution, see HOPE
  gamma(, β) density is g(λ) = C λα-1e-λβ
  mean =  / β
  variance =  / β2
  100p percentile = GAMMAINV(p, , 1/) or
  GAMMAINV(p, , 1)/
  Excel uses 1/ β instead of β as the second parameter
    β is in units of time

## Slide 45: Poisson Likelihood – Gamma Conjugate Prior
  SAPHIRE uses mean and  (called “r” by SAPHIRE)
  Example gamma distributions:
Pages A-18 through A-20

## Slide 46: Poisson Likelihood – Gamma Conjugate Prior
If X is Poisson( t) and gprior() is gamma(prior , βprior), then posterior distribution of λ is
  gamma(post , βpost )
    post = prior + x (x = # events)
    βpost = βprior + t (t = observation time)
    prior is like prior number of events
    prior is like prior observation time
  Therefore, posterior mean = (prior + x)/(βprior + t)
    Again, a weighted average of MLE, x/t,
    and prior mean, prior / βprior
Pages 6-12, 6-13
Notes: Prove this heuristically by writing posterior as product of prior and likelihood. Don’t worry about normalization constant.

## Slide 47: DSW Poisson-Gamma Bayesian Example
Assume our prior is ~Gamma(2, 340 hr)
Assume we see 0 failures in 870 hours
Step 1 – Specify the Prior (Gamma Tab)
Step 2 – Specify Data (Bayes-Poisson)

## Slide 48: DSW Poisson-Gamma Bayesian Example
Read the results

## Slide 49: Exponential Likelihood – Gamma Conjugate Prior
If T1,…,Tn are independent observations from exponential(λ) distribution and gprior() is gamma(prior, βprior), then posterior distribution of λ is
    gamma(post, βpost)
      post = prior + n (n = # events)
      βpost = βprior + Σti (ti = observed times of n events)
Again, for a gamma(, β) distribution
  mean =  / β
  variance =  / β2
  100p percentile = GAMMAINV(p, , 1/)
Page 6-61

## Slide 50: DSW Exponential-Gamma Bayesian Example
Assume our prior is ~Gamma(2, 340 hr)
Assume we tested five components and saw times-to-failure of: 205, 100, 760, 450, 1100 hours
Step 1 – Specify the Prior (Gamma Tab)
Step 2 – Specify Data (Bayes-Exponential)

## Slide 51: DSW Exponential-Gamma Bayesian Example
Read the results

## Slide 52: DSW Steps for Solving Inference Problems
What is the model?
  Choose a model (distribution) based on the failure mode and evidence
What is the prior?
  Choose the prior distribution and enter the parameters in the appropriate distribution tab
What is the evidence?
  Choose the Bayesian inference tab for the type of prior and enter the evidence
Specify low and high values in the calculation section to answer questions

## Slide 53: LOSP Example

## Slide 54: Prior Distributions for LOSP Example (For Later Reference)
 LOSP ~ gamma(1.58, 43.96 reactor-critical years)
  From “Reevaluation of Station Blackout Risk at Nuclear Power Plants: NUREG/CR-6890, December 2005
  This is the composite from several subtypes of LOSP event
pFTS ~ beta(0.957, 190)
  From S. A. Eide, “Historical Perspective On Failure Rates for US Commercial Reactor Components,” Reliability Engineering and System Safety, 80 (2003), pp. 123-132
 FTR ~ gamma(1.32,1137 hrs)
  From Eide (2003)
  This is the composite of two rates

## Slide 55: Prior Density Plots: LOSP
LOSP
(per reactor-critical year)
LOSP
pdf, f()
gamma(1.58, 43.96 reactor-critical years)

## Slide 56: Prior Density Plots: FTS
pFTS
pFTS
pdf, f(p)
beta(0.957, 190)

## Slide 57: Prior Density Plots: FTR
FTR
(per hour)
pdf, f()
FTR
gamma(1.32,1137 hrs)

## Slide 58: LOSP Example Data
The observed number of LOSP events over a period of time
  1 initiating event in 9.2 operating years
The observed number of failures out of a number of demands
  1 failure to start in 75 demands
The observed number of failures in an observed total operating time
  0 failures to run in 146 running hours

## Slide 59: LOSP Frequency Update with DSW
For LOSP frequency, aleatory model is Poisson
  Specify prior (Gamma tab)~gamma(1.58, 43.96 rcy)
  Bayesian update, so select “Bayes-Poisson” tab
Distribution Summary Worksheet – Ver 1i.xlsx

## Slide 60: EDG FTS Update with DSW
For EDF fails to start, aleatory model is Binomial
  Specify prior (Beta tab)~beta(0.957, 190)
  Bayesian update, so select “Bayes-Binomial” tab
Distribution Summary Worksheet – Ver 1i.xlsx

## Slide 61: EDG FTR Update with DSW
EDG fails to run, aleatory model is Poisson
  Specify prior (Gamma tab) ~gamma(1.32,1137 hrs)
  Bayesian update, so select “Bayes-Poisson” tab
Distribution Summary Worksheet – Ver 1i.xlsx

## Slide 62: Summary of Bayesian Estimates for LOSP Example
Parameter | Distribution | Point Est. (Mean) | 90% Interval | Distribution
LOSP | Industry Prior Posterior | 3.6E-2 yr -1 4.9E-2 yr -1 | (4.6E-3, 9.2E-2) yr -1 (1.1E-2, 1.1E-1) yr -1 | Gamma(1.58, 43.96) Gamma(2.58, 53.16)
pFTS | Industry Prior Posterior | 5.0E-3 7.4E-3 | (2.3E-4, 1.5E-2) (1.3E-3, 1.8E-2) | Beta(0.957, 190) Beta(1.957, 264)
FTR | Industry Prior Posterior | 1.2E-3 hr -1 1.0E-3 hr -1 | (1.1E-4, 3.2E-3) hr -1 (9.6E-5, 2.8E-3) hr -1 | Gamma(1.32, 1137) Gamma(1.32, 1283)
        Posterior credible intervals generally are shorter than those from data alone (i.e., confidence interval) or prior alone (prior credible interval)

## Slide 63: Comparison of Posterior and Prior: LOSP
LOSP

## Slide 64: Comparison of Posterior and Prior: FTS
pFTS

## Slide 65: Comparison of Posterior and Prior: FTR
FTR

## Slide 66: LOSP Updates with RADS Calculator
RADS (Reliability and Availability Data System) was developed for NRC by INL
Both stand-alone version and web-based calculator
Will show web-based calculator in this course
Access calculator at
https://nrcoe.inl.gov/radscalc/Default.aspx

## Slide 67: LOSP Updates with RADS Calculator

## Slide 68: LOSP Update with RADS Calculator
Menu options across the screen
  Select Analysis of Unpartitioned Data
    Bayes Analysis

## Slide 69: LOSP Update with RADS Calculator
For LOSP frequency, select “Failure Rate”
Enter data
  “Number of Failures”
  “Exposure Time”
    Units are not specified
Click the “Prior Distribution” bar towards bottom-left
  Select gamma prior ~gamma(1.58, 43.96)
  Enter “a” (alpha=1.58) and “b” (beta=43.96)
Press “Calculate Bayes”

## Slide 70: RADS Calculator results

## Slide 71: LOSP Update with RADS Calculator
For EDG failure to start, select “Demand Probability”
Enter data
  “Number of Failures”
  “Number of Demands”
Select beta prior and enter “a” (alpha) and “b” (beta)
Press “Calculate Bayes”

## Slide 72: EDG FTS Update with RADS Calculator

## Slide 73: Noninformative PRIORS

## Slide 74: Noninformative (Formal) Prior Distributions
The original intent of “noninformative” priors was to answer question
  How do we find a prior representing complete ignorance?
Rev. Bayes suggested a uniform prior
  Laplace used this in his activities with great success
  But, there are philosophical/mathematical problems with this

## Slide 75: Noninformative (Formal) Prior Distributions
Sir Harold Jeffreys suggested a prior that was invariant to changes in
  Scale
  Location
Consequently, so-called “noninformative” prior is typically not uniform for the parameter of interest
  It is uniform (or approximately so) for some transformed parameter
  Instead, it depends on the process generating the data
  Has property that the Bayes posterior intervals are approximately equal to frequentist confidence intervals (exactly equal for continuous data)
    Formal priors “let the empirical data speak for themselves”
Notes: In standard PRA usage, “noninformative prior” means Jeffreys prior.

## Slide 76: Noninformative (Formal) Prior Distributions
Other formal priors have been developed
Often used as “objective” or reference prior
  Also called “vague” or “diffuse” prior
  Jeffreys prior is most common choice of formal prior for single-parameter problems
Sir Harold Jeffreys
Knight Bachelor for applied mathematics and astronomy. Interestingly, he was a plate tectonics denier.
Notes: Mathematician and geophysicist, Jeffreys was honored as a Knight Bachelor for applied mathematics and astronomy. Interestingly, he was a plate tectonics denier.

## Slide 77: Jeffreys Prior Distributions
For binomial(n, p) aleatory model
  Jeffreys noninformative prior for p is beta(1/2, 1/2), which is a proper prior (integral equals 1)
For Poisson(t) aleatory model
  Jeffreys noninformative prior for  can be thought of as
  gamma(1/2, 0) (improper prior, integral diverges)
For exponential() aleatory model
  Jeffreys noninformative prior for  can be thought of as gamma(0, 0) (improper prior, integral diverges)
Pages B-12 through B-14, 6-14, 6-37, 6-61, 6-62

## Slide 78: Jeffreys Prior Distributions
Two of these priors look like
gamma(1/2, 0) beta(1/2, 1/2)
Binomial Model
Poisson Model

## Slide 79: Updating Jeffreys Prior Distributions
For binomial(n, p) aleatory model
  Jeffreys noninformative prior for p is beta(½, ½)
  Posterior is beta(x + ½, n – x + ½)
For Poisson(t) aleatory model
  Jeffreys noninformative prior for  is gamma(½, 0)
  Posterior is gamma(x + ½, t)
For exponential() aleatory model
  Jeffreys noninformative prior for  is gamma(0, 0)
  Posterior is gamma(n,  ti)

## Slide 80: Jeffreys Prior Distributions
Let us compare results from these priors to frequentist confidence intervals

## Slide 81: Using DSW to Update Jeffreys Prior Distributions
Select appropriate tab (e.g., Bayes-Binomial)
Enter observed data (e.g., 1 failure in 75 demands)
Read off posterior from column labeled “Jeffreys”

## Slide 82: Using RADS Calculator to Update Jeffreys Prior Distributions
Select “Jeffreys noninformative” as prior distribution
Enter observed data
Press “Calculate Bayes”

## Slide 83: Data Versus Prior Distribution
As amount of data increases, prior becomes less important
Siu and Kelly, 1998
Gamma (1/2,0)

## Slide 84: Constrained Noninformative (CNI) Prior
Recall that Jeffreys prior for binomial likelihood is beta(½, ½)
  The prior mean is 0.5 (quite large if a failure prob.)
With sparse data, prior mean can influence results too much
To overcome this, can use prior which has specified mean, but is close to Jeffreys prior otherwise
  Specified mean might be industry average value
Result is called “constrained noninformative” (CNI) prior
Left to right: Claude Shannon, Edward Jaynes, Corwin Atwood
Notes: CNI prior is a maximum entropy prior, using Jaynes’ definition of entropy as the Kullback-Leibler deviation from the reference NI prior. In this case (contrary to Jaynes), the reference NI prior is taken to be the Jeffreys prior.

## Slide 85: Constrained Noninformative Prior
Cannot be written in form of standard distribution for case of binomial likelihood
  Approximated well by beta distribution with α = 0.5
    See Table C.8 in HOPE for precise values of α
  For the beta, the mean = α / (α + β), β can be found to be
    β = α(1-mean)/mean
For Poisson likelihood, CNI prior is gamma(½, 1/(2*mean))
For exponential likelihood, cannot define CNI prior, as it is not proper, therefore cannot have finite mean
  Alternative is maximum entropy prior, which is
    Gamma(1, 1/mean)
    This is an exponential distribution

## Slide 86: Updating CNI Prior with DSW
Is conjugate for Poisson and binomial data
Enter specified mean value
Enter data observed
Read off posterior results in column labeled “CNI”
Example: assume mean probability of EDG failure to start is thought to be 0.01
  Take this as mean of CNI prior and update with 1 failure in 75 demands

## Slide 87: Updating CNI Prior with DSW
Results

## Slide 88: Updating CNI Prior with RADS Calculator
Input parameters of beta or gamma CNI prior, as appropriate
Press “Calculate Bayes”

## Slide 89: Nonconjugate Priors

## Slide 90: Nonconjugate Priors
For each aleatory model, there is at most one conjugate prior type
  All other distributional forms are nonconjugate
  Integral in denominator of Bayes’ Theorem must be done numerically
Most common nonconjugate prior in PRA is lognormal distribution
  Originally used in WASH-1400 to represent plant-to-plant variability in parameter values
  Very convenient when uncertainty spans several orders of magnitude
  Useful in expert elicitation (e.g., seismic PRA, NUREG-1829)
    Elicit median and upper bound, 5th and 95th percentiles, etc.

## Slide 91: Nonconjugate Prior Distributions – The Concept
Generic databases often express uncertainty in terms of lognormal distribution
Experts often provide order-of-magnitude estimates, represented well by lognormal distribution
For these or other reasons, we may prefer a nonconjugate prior
When prior is not conjugate
  Posterior distribution must be found by numerical integration. Will use online RADS calculator.
Pages 6-16 through 6-20, 6-39 through 6-43

## Slide 92: Lognormal Distribution
Definition of a lognormal distribution:
  X is lognormal(μ, σ2) if ln(X) is normal(μ, σ2)
Will encounter lognormal distribution in various areas of risk assessment
  Often used as a prior distribution in PRA, even though it is not conjugate
  Sometimes used as likelihood function (e.g., LOSP recovery time)
    Covered in P-501 and P-502 courses
  Often used to model hazard (earthquake frequency) and fragility (probability of seismic failure) in seismic PRA
Pages A-16, A-17

## Slide 93: Facts About the Lognormal Distribution
Median of X is eμ Mean of X is exp[ + (½)2]
Variance of X is (mean)2[exp(2) – 1]
Error factor (EF) is defined as e1.645σ
Other ways to write EF (applies only to lognormal)
  EF = 95th/50th = 50th/5th = (95th/5th)1/2
Probability
where Ф is tabulated in HOPE, Appendix C
  Can also use =LOGNORMDIST(x, , ) in Excel
  or =NORMDIST(LN(x), , , TRUE)
Percentile
  Can use =LOGINV(p, , ) in Excel
Notes: Point out that mean is always > median

## Slide 94: Lognormal Distribution
Lognormal distribution is determined (in general) by any two of
  μ
  σ2
  median
  mean
  variance
  EF or upper percentile
SAPHIRE uses mean and EF

## Slide 95: Lognormal Distribution in DSW
Parameterized using μ and σ
Sheet also includes “lognormal calculator” when given
  Mean & EF
  Median & EF
  Mean and standard deviation
    These return μ and σ

## Slide 96: Updating Lognormal Prior with RADS Calculator
Example: Interested in failure on demand for standby pump
Generic database shows p is lognormal with
  mean of 0.003
  error factor of 10
Observe 0 failures in 36 demands
What is posterior mean of p?

## Slide 97: Updating Lognormal Prior with RADS Calculator
Select “Demand Probability” and enter input data in usual way
Select “Lognormal” as the prior distribution and enter mean and error factor
Push “Calculate Bayes”
Note that posterior distribution is not lognormal

## Slide 98: Updating Lognormal Prior with RADS Calculator

## Slide 99: Lognormal (cont.)