## Slide 1: Section 5: Uncertainty Propagation in Risk Assessment
Purpose
  Illustrate, using Excel, how epistemic uncertainties in parameters are propagated through PRA models to obtain Bayesian estimates of risk metrics
Objectives
  Through examples using Excel, students will learn about
    Monte Carlo sampling from distributions
    Estimation of a “top event” probability or sequence frequency by propagation of distributions through a logic model
    Simple Monte Carlo sampling and Latin Hypercube sampling

## Slide 2: Risk
Recall the three questions a risk analysis attempts to answer:
  What undesired things could happen?
  What are their probabilities or frequencies?
  What are their consequences?
Must quantify answers, and assess uncertainty in these answers
In LOSP example
  Events
    Initiating event could occur
    Then EDG power system could successfully operate or it could fail
  Consequences
    Plant trip likely, perhaps worse if EDGs fail
  Frequency of bad consequence is subject of this section
Stan Kaplan
John Garrick

## Slide 3: Overall Approach to Uncertainty Propagation
In risk assessment, we estimate
  Probability of “top event” (if looking at fault trees)
  Frequency of “end state” (if looking at event trees)
These estimates are typically based upon “minimal cut sets”
  Minimal cut sets contain parameters such as
    Failure rates
    Probabilities of failure on demand
  In the LOSP example, we develop SBO as a (fairly complicated) function of LOSP, pFTS, and FTR
  We approximate the Bayes distribution of the end-state frequency as follows

## Slide 4: Overall Approach to Uncertainty Propagation
Randomly sample a value of each basic parameter
  This sample comes from the parameter’s posterior distribution
Samples are used to quantify a desired
  Top-event probability
  End-state frequency
This process is repeated many times
  Use new sampled values of the basic parameters on each iteration
  Obtain many calculated values of desired result
  Resulting values are a (pseudo)random sample from the Bayesian distribution of the top-event probability or end-state frequency
    Together, they approximate the resulting distribution

## Slide 5: Example
Evaluate fault tree to determine cut sets
  Single cut set  A*B
In Excel, create samples for A, B
Use samples to sample top event
  MY-TOP = A × B
Use MY-TOP samples to produce
  E[ ]
  Percentiles
  Distribution
  …

## Slide 6: LOSP Example
Loss of
Offsite Power
Diesel Generator System Failure
Diesel Generator System Success

## Slide 7: LOSP Example
Note that LOSP is just one initiating event…this analysis process is carried out for all results from all initiating events
LOSP, trip, etc.

## Slide 8: PRA Minimal Cut Sets
In every minimal cut set there are “basic events”
Every basic event stored in PRA database typically has some epistemic uncertainty about the value used for the event
  The propagation of this uncertainty through cut sets must be performed in order to understand the uncertainty in the overall result (e.g., CDF)
  This uncertainty can be characterized via summary measures, such as mean value and 95th percentile

## Slide 9: Schematic View of Uncertainty Propagation

## Slide 10: Minimal Cut Sets in LOSP Example
SBO = LOSP × Pr[EDG system fails]
Pr[EDG system fails]
  = Pr[(FTSA and FTSB ) or (FTSA and FTRB )
  or (FTSB and FTRA ) or (FTRA and FTRB )]
   Pr(FTSA and FTSB ) + Pr(FTSA and FTRB )
  + Pr(FTSB and FTRA ) + Pr(FTRA and FTRB )
  Using rare event approximation, Pr[EDG system fails]:
  = Pr(FTSA)×Pr(FTSB) + Pr(FTSA)×Pr(FTRB)
  + Pr(FTSB)×Pr(FTRA) + Pr(FTRA)×Pr(FTRB)
  assuming EDGs A and B fail independently
Notes: We do not treat common-cause failure in this class. It is covered in the later System Modeling class.

## Slide 11: Minimal Cut Sets in LOSP Example
Generic forms for basic event probabilities
  Demand Based uses probability of failure
    Pr(FTS) = pFTS
  Rate Based requires rate * mission time
    Pr(FTR) = 1 – ≈ FTRtmission
Component probabilities are updated ~ every two years
  NUREG/CR-6928, Industry Average Parameter Estimates
  http://nrcoe.inel.gov/resultsdb/AvgPerf/

## Slide 12: Minimal Cut Sets in LOSP Example
Pr(FTSA)×Pr(FTSB ) = ?
  pFTS2 ?
    one estimated parameter (correlated)
  pFTS-A ×pFTS-B ?
    two estimated parameters (uncorrelated)
Note that 100% correlation means the components have the exact same probability of failure. It does not mean that they will fail at the exact same time.
  More to come on correlation

## Slide 13: Minimal Cut Sets in LOSP Example
Boolean
  “Sets” FTSA ∩ FTSB
Quantify
  Independent?  YES
  Pr(Cut Set) = Pr(FTSA)* Pr(FTSB)
Monte Carlo
  P(Cut Set) = PA*PB = (PA)2

## Slide 14: How Many Distinct Parameters in Example?
If we distinguish between pFTS-A and pFTS-B
  Assumes that the two p’s differ significantly
  Use only data from ith EDG to estimate pFTS-i
    Have relatively more uncertainty in each estimate
    Same prior for each pFTS-i ?
If we model only a single pFTS
  Assumes that the two p’s are nearly equal
  Uses data from both EDGs, and generic prior, to estimate the one p
    Have relatively less uncertainty in the one estimate
    Use generic prior

## Slide 15: How Many Distinct Parameters in Example?
If we assign independent Bayes distributions to pFTS-A and pFTS-B
  E(pFTS-A×pFTS-B) = E(pFTS-A)×E(pFTS-B)
If we assign Bayes distribution to pFTS
  E(pFTS2) > E(pFTS)×E(pFTS)
So if the two parameters are really the same
  Modeling them with independent distributions (uncorrelated sampling) yields too small a mean.
In SAPHIRE, to force pFTS-A and pFTS-B to equal each other, i.e. to equal pFTS
  Assign them to a single correlation class.
For additional information, see (Apostolakis and Kaplan, 1981)

## Slide 16: Un- versus Correlated Example
OR gate with
10 inputs
Each inputs is
~beta(1, 95)
Mean=0.01
Correlated
Uncorrelated

## Slide 17: SBO Frequency in LOSP Example
Assume single pFTS, single FTR
  PrFTR = 1 – ≈ FTRtmission
SBO ≈ LOSP ×[pFTS2 + 2pFTS FTRtmission + (FTRtmission)2]
Approximate the Bayes distribution of SBO
by a (large) random sample from the
distribution.
losp demo problem.xls

## Slide 18: Uncertainty Analysis for Other Applications

## Slide 19: Propagation of Uncertainty
To perform uncertainty analysis, the analyst must specify:
  The type of sampling
    Simple Monte Carlo sampling (SMCS)
      Called “Monte Carlo” in SAPHIRE
    Latin hypercube sampling (LHS)
    Grid sampling (not discussed in this course)
  The number of iterations (i.e., samples)
    For example, if we specify 2,000 samples and there are 10 unique basic events, we generate 20,000 random numbers
  The random number generator seed value

## Slide 20: Two Kinds of Sampling
Simple Monte Carlo Sampling (SMCS)
In simple Monte Carlo sampling, each parameter is sampled (pseudo)randomly from its specified distribution
  Each set of sampled values is entered into the minimal cut sets
  The frequency/probability of the top event is calculated for each set of sampled values
  This process is repeated many times (up to the number of samples specified)

## Slide 21: Two Kinds of Sampling
Latin Hypercube Sampling (LHS)
In Latin hypercube sampling, each parameter is sampled in a stratified way, to guarantee that each portion of the range of the distribution is represented
An example with 10
stratifications is shown
  Within each portion,
  we randomly sample

## Slide 22: Latin Hypercube Sampling
For example, let us denote one parameter by p
  Bayesian distribution of p is known: the posterior distribution of p based on prior information and relevant data
  If 10 samples were to be taken
    p would be sampled randomly from interval (p0.0, p0.10), giving a value that we denote as p1
    Again, sample randomly from interval (p0.10, p0.20), giving a value that we denote at p2
    Repeat process until we have p10 [from interval (p0.90, p1.0)]
  This is stratified sampling, in which the sampled points are forced to cover entire range of the distribution

## Slide 23: Latin Hypercube Sampling
After all parameters in the model have been sampled in this stratified way, they are randomly matched to each other
  In example with LOSP, pFTS, and FTR, one of the sampled values of each parameter would be chosen
  However, they would be chosen so that the largest value of one parameter is not necessarily matched with largest or smallest values of other parameters
  Instead, the choice of each pairing is random
  For the chosen values, the top-event is calculated
  Then another set of sampled parameter values is chosen, using values that have not been chosen yet
In this way, a number (10 in this example) of values are calculated for the end-state frequency

## Slide 24: Differences Between Sampling Types
While there are computational differences between the two techniques (SMCS and LHS):
  One should not be too concerned about which technique is selected for a particular analysis
  Instead, one should be concerned about convergence of the numeric calculation
  Convergence may be checked by noting change (or lack thereof) of uncertainty results as the number of samples increases
The samples from either method converge to the Bayes distribution of the end-state frequency or top-event probability

## Slide 25: The Seed Value
A seed value tells software where, in sequence of possible random numbers, to start selecting random numbers
  The random number generator gives a sequence of “random” integers (which are typically converted to real numbers)
  A seed of “51” may tell us to start at the ith random integer
  A seed of “1,236” may tell us to start at the jth random integer
  etc.
Again, checking for convergence should make seed selection irrelevant
  But, to reproduce analysis results, one must use the same seed and same number of samples

## Slide 26: Accuracy of Sampling
Accuracy of a simple random sample is roughly proportional to square root of sample size
  For example, if SBO is sampled from its distribution n times
    Mean of the distribution is estimated by average of n sampled values (the sample mean), and this average has standard deviation proportional to
    Estimate of this quantity is the standard error
      A confidence interval equals the sample mean  a multiple of the standard error
LHS is more complicated than simple random sampling
  But requires fewer samples for comparable accuracy
  Therefore, it is justified if each calculation of top-event is expensive or time-consuming

## Slide 27: Uncertainty Analysis Results
Every result from the PRA is uncertain
  Parameters used to quantify basic events (p for FTS,  for FTR, etc.)
  Initiating event frequency
  System failure probability
  Overall results such as core damage frequency and importance measures